## Sheet1
Area Calculation
| Storage Tank |  |  | Bund wall
| Diameter (m) | 50 |  | Rectangular | Length | 100
|  | 2 |  |  | Width | 80
| Radius (m) | 25 |  |  | Height | 5
| π (Pi) | 3.1416
| Height (m) | 5 |  |  | Area (m2) | 8000
[5 empty] | Volume (m3) | 40000
| Area (m2) | 1963.4954
| Volume (m3) | 9817.477 |  | Square | Side | 100
[5 empty] | Height | 5
[5 empty] | Area (m2) | 10000
[5 empty] | Volume (m3) | 50000
Storage Tank
Required Foam Concentrate: Area x Application Rate x Foam Mixing Ratio x Discharge Time
Type of Hydrocarbon | Foam Concentrate Required (Liters) | Application Rate (L/m2/min) | Foam Mixing Ratio | Discharge Time (Minutes)
Flash point between 100°F and 140°F (38°C and 60°C) | 19144.0802 | 6.5 | 0.03 | 50
Flash point below 100°F (38°C) or liquids heated above their flash points | 24887.3043 | 6.5 | 0.03 | 65
Crude petroleum | 24887.3043 | 6.5 | 0.03 | 65
Bund Wall (Rectangular)
Required Foam Concentrate: Area x Application Rate x Foam Mixing Ratio x Discharge Time
Type of Hydrocarbon | Foam Concentrate Required (Liters) | Application Rate (L/m2/min) | Foam Mixing Ratio | Discharge Time (Minutes)
Flash point between 100°F and 140°F (38°C and 60°C) | 78000 | 6.5 | 0.03 | 50
Flash point below 100°F (38°C) or liquids heated above their flash points | 101400 | 6.5 | 0.03 | 65
Crude petroleum | 101400 | 6.5 | 0.03 | 65
Bund Wall (Square)
Required Foam Concentrate: Area x Application Rate x Foam Mixing Ratio x Discharge Time
Type of Hydrocarbon | Foam Concentrate Required (Liters) | Application Rate (L/m2/min) | Foam Mixing Ratio | Discharge Time (Minutes)
Flash point between 100°F and 140°F (38°C and 60°C) | 97500 | 6.5 | 0.03 | 50
Flash point below 100°F (38°C) or liquids heated above their flash points | 126750 | 6.5 | 0.03 | 65
Crude petroleum | 126750 | 6.5 | 0.03 | 65
Bund Wall (Rectangular) minus Storage Tank Area
Required Foam Concentrate: Area x Application Rate x Foam Mixing Ratio x Discharge Time
Type of Hydrocarbon | Foam Concentrate Required (Liters) | Area (m2) | Application Rate (L/m2/min) | Foam Mixing Ratio | Discharge Time (Minutes)
Flash point between 100°F and 140°F (38°C and 60°C) | 58855.9198 | 6036.5046 | 6.5 | 0.03 | 50
Flash point below 100°F (38°C) or liquids heated above their flash points | 76512.6957 | 6036.5046 | 6.5 | 0.03 | 65
Crude petroleum | 76512.6957 | 6036.5046 | 6.5 | 0.03 | 65
Bund Wall (Square) minus Storage Tank Area
Required Foam Concentrate: Area x Application Rate x Foam Mixing Ratio x Discharge Time
Type of Hydrocarbon | Foam Concentrate Required (Liters) | Area (m2) | Application Rate (L/m2/min) | Foam Mixing Ratio | Discharge Time (Minutes)
Flash point between 100°F and 140°F (38°C and 60°C) | 78355.9198 | 8036.5046 | 6.5 | 0.03 | 50
Flash point below 100°F (38°C) or liquids heated above their flash points | 101862.6957 | 8036.5046 | 6.5 | 0.03 | 65
Crude petroleum | 101862.6957 | 8036.5046 | 6.5 | 0.03 | 65

## Sheet2
NFPA 11 Chapter 5 |  |  |  | Foam Mixing Ratio
Table 5.2.4.2.2 Foam Handline and Monitor Protection for Fixed-Roof Storage Tanks Containing Hydrocarbons |  |  |  | 1% | 3% | 6% | Other
Hydrocarbon Type | Minimum Application Rate |  | Minimum Discharge Time (minutes) | 99% | 97% | 94% | Other
| gpm/ft2 | mm/min*
Flash point between 100°F and 140°F (38°C and 60°C) | 0.16 | 6.5 | 50 | Other Application Rates
Flash point below 100°F (38°C) or liquids heated above their flash points | 0.16 | 6.5 | 65 | 4.1 | 6.5 | 12.2 | Other
Crude petroleum | 0.16 | 6.5 | 65
|  | Other | Other
Notes: * L/min·m2 is equivalent to mm/min.